## Slide 1: The value of Ensembles on planning the energy system for the future
November 2018
Presented BY Daniel Guppy

## Slide 2: Agenda
Temperature drives demand
Temperature de-rates supply and network assets
Using CCiA data understand future extreme operating conditions
  Temporally downscale daily climate data
  Consider impact of temperature on supply and demand

## Slide 3: Temperature drives demand Extreme temperature drives extreme demand

## Slide 4: Temperature drives demand

## Slide 5: Temperature drives demand
Heatwave
Low – three days above 30
High – three days above 32.5
Extreme – three days above 35

## Slide 6: Temperature de-rates generation

## Slide 7: Temperature de-rates generation
Thermal generation – typical gas turbines begin to de-rate at 35˚C and can de-rate as much as 5% and 8% for ambient temperatures of 40˚C and 45˚C, respectively. Sustain periods of high temperatures impact generators ability to cool.
Solar farms – some utility power system inverters de-rate around 10% when operating at 50˚C. Inverters operating in the distribution network can also de-rate by 10% or more at 50˚C.
Wind farms – typical wind farm turbines in the NEM experience 100% de-rating for temperatures between 35˚C and 45˚C, and will return to service when the temperature drops around 1˚C to 5˚C from the cut-out temperature.
Source: AEMO 2018 ISP

## Slide 8: Temperature de-rates generation
NEM generation density map

## Slide 9: Temperature de-rates networks

## Slide 10: Temperature de-rates networks
Transmission lines – short-term transfer capability can be reduced up to 14% for a temperature increase from 35˚C to 40˚C. For 500 kV lines, this reduction can be as high as 250 MW. Conductors expand at high temperatures, and at extreme temperatures are at risk of irreversible expansion, resulting in permanent reduced capability.
Power electronics – the Basslink DC interconnector between Victoria and Tasmania automatically limits capacity progressively when ambient temperatures at Loy Yang reach 43˚C or above, or when temperatures at George Town reach 33˚C or above.
Source: AEMO 2018 ISP

## Slide 11: Temperature de-rates generation
NEM transmission assets map

## Slide 12: Using CCiA data understand future extreme operating conditions

## Slide 13: Using CCiA data understand future extreme operating conditions
Quantile-Quantile matching for temporal downscaling
  Collect daily min/max temperature projection data from CCiA for each ensemble member in the forecast horizon (2018-2050)
  Collect historical actual half-hourly temperature station observations and calculate daily minimum, median and maximum (1998-2018)
  Calculate the empirical temperature CDF of projected daily temperatures data
  Calculate the empirical temperature CDF of historical daily observations
  Map historical temperature quantiles to projected temperature quantiles and assign a scaling factor
  Interpolate daily scaling factors to half-hourly and scale
  AEMO treats each historical year scaled to each ensemble member as a simulation of future weather.
  Final table is 20 historical years x 8 models x 32 forecast weather years

## Slide 14: Using CCiA data understand future extreme operating conditions
ClimateChangeInAustralia.gov.au
AEMO Use:
Daily Stations data
Daily average, minima and maxima temperature data
8 different climate models in Ensemble
Temperature Threshold Calculator

## Slide 15: Using CCiA data understand future extreme operating conditions
Quantile match historical daily max temperature station data to model data

## Slide 16: Using CCiA data understand future extreme operating conditions
NSW - Temperature 6 and 7 Feb 2000 vs 6 and 7 Feb 2030

## Slide 17: Using CCiA data understand future extreme operating conditions
Global climate ensemble models vs station temperature data for same overlapping time period

## Slide 18: Using CCiA data understand future extreme operating conditions
Extreme temperature average for 1995 (left) and projected for 2070 (right) in eastern Australia
Source: AEMO 2018 ISP and CCiA threshold calculator

## Slide 19: Using CCiA data understand future extreme operating conditions
Maximum demand Probability of Exceedance forecasting
demand = f(weather)
Probabilistic distribution of weather drives the probabilistic distribution of energy demand

## Slide 20: Questions